## 01 General
SURGE (WATER HAMMER) ANALYSIS — INPUT DATA SHEET
Standard data collection sheet for surge / transient analysis of water transmission mains. Light blue = to be filled in; light grey = calculated automatically. Fields marked with an asterisk * are mandatory; every other field may be left blank if not available.
* = MANDATORY — must be filled in (darker blue shading). All other fields are optional.
1. PROJECT INFORMATION
Parameter | Value | Unit | Notes
Project Name |  | — | e.g. Rewa River Water Supply Scheme
Sub-project / Pipeline |  | — | e.g. DN900 Treated Water Rising Main, Stage I
Route / Chainage Range |  | — | e.g. Ch 0+000 WTP clearwell to Ch 7+500 Waitolu Reservoir
Design Stage |  | — | select from list
Type of Analysis |  | — | select; if several, describe in the remarks
Analysis Software / Method |  | — | e.g. KYPipe Surge / Bentley HAMMER / PIPE2008 / in-house code
Prepared By / Contact |  | — | for queries during modelling
Date |  | — | format YYYY-MM-DD
Total Pipeline Length L |  | m | linked from sheet ‘04 Pipeline Profile’, do not type
Upstream Pipe Centreline Level |  | m | linked from the first entered node
Downstream Pipe Centreline Level |  | m | linked from the last entered node
2. GLOBAL COMPUTATION PARAMETERS
Parameter | Value | Unit | Notes
Design Capacity Q |  | m³/d | nameplate capacity of the scheme
Design Flow Qc |  | m³/h | flow used for the surge run; state the pump combination
Fluid |  | — | select from list
Water Temperature T | 20 | °C | affects vapour head and wave speed
Density ρ | 998.2 | kg/m³ | clean water at 20 °C
Bulk Modulus of Elasticity K | 2.18 | GPa | ≈ 2.18 GPa for water at 20 °C
Kinematic Viscosity ν | 1.006 | mm²/s | ≈ 1.006 at 20 °C
Vapour Pressure (absolute) | 2.34 | kPa | ≈ 2.34 kPa at 20 °C; governs column separation
Acceleration of Gravity g | 9.81 | m/s²
Friction Model |  | — | select from list
Roughness Coefficient C / Height Δ |  | C / mm | HW C: new steel & DI ≈ 120–130, PE ≈ 140–150; or give absolute roughness
Wave Speed a |  | m/s | leave blank to back-calculate from pipe material & wall thickness. Typical: steel 1100–1200, DI 1100–1200, PE 300–400
Simulation Duration |  | s | ≥ 20 L/a is recommended, or 3–5 times the pump run-down time
Minor Losses |  | — | select from list
Remarks |  | — | any other assumption the model shall honour

## 02 Pump Data
PUMP SET DATA
One row per pump type; units of the same type may be grouped and their number entered under “Qty Installed”. Grey columns are calculated — please do not overwrite. Fields marked * are mandatory (duty/standby, Qn, Hn, n, η); every other field may be left blank.
* = MANDATORY — must be filled in (darker blue shading). All other fields are optional.
SN | Location / Unit ID | Pump Model | Qty Installed | Duty / Standby * | Rated Flow Qn * (m³/h) | Rated Head Hn * (m) | Rated Speed n * (rpm) | Rated Efficiency η * (%) | Shaft Power Psh (kW) | Motor Rating (kW) | Rotating Inertia J (kg·m²) | Flywheel Effect GD² (kg·m²) | Remarks
Note: J should cover pump rotor + motor rotor + coupling as one rotating train. GD² = 4J is provided for programs that take flywheel effect directly. Please attach the Q-H and Q-η curves, and ideally the four-quadrant characteristic curves, with this sheet.
SUPPLEMENT: DISCHARGE VALVE & CLOSING LAW (essential input for surge protection)
SN | Location / Unit | Valve Type | Fast Closing Time (s) | Closes To (deg) | Slow Closing Time (s) | Total Closing Time (s) | Remarks

## 03 Reservoir Levels
BOUNDARY WATER LEVELS
All levels shall be referred to one common datum (state the datum in the remarks). “Design W.L.” is the level normally used for the surge run; it is mandatory for the upstream suction well and for the downstream delivery tank. Every other field may be left blank.
* = MANDATORY — must be filled in (darker blue shading). All other fields are optional.
1. UPSTREAM BOUNDARY (suction well / clearwell / intake tank)
Structure Name | Chainage | Tank Bottom Level (m) | Max. W.L. (m) | Design W.L. * (m) | Min. W.L. (m) | Head above W.S. (m abs) | Remarks
2. DOWNSTREAM BOUNDARY (outlet tank / treated water reservoir / consumer)
Structure Name | Chainage | Tank Bottom Level (m) | Max. W.L. (m) | Design W.L. * (m) | Min. W.L. (m) | Head above W.S. (m abs) | Remarks
3. INTERMEDIATE NODES (off-takes, elevated tanks, critical pressure points — if any)
Node Name | Chainage | Node Type | Node Level (m) | Min. Allowable Pressure (m) | Max. Allowable Pressure (m) | Node Demand (m³/h) | Remarks
Note: the maximum and minimum water levels define the worst-case envelopes — commonly “low level + high flow” governs downsurge, “high level + low flow” governs upsurge.

## 04 Pipeline Profile
PIPELINE PROFILE (Chainage — Elevation — Diameter)
List every node from upstream to downstream without leaving blank rows. Distance is measured along the route from the first node. Grey columns are calculated. Chainage and centreline elevation Z are mandatory for every node; every other field — including the cumulative distance L — may be left blank.
* = MANDATORY — must be filled in (darker blue shading). All other fields are optional.
SN | Chainage * (station) | Distance L (m) | Step from Previous (m) | Centreline Elev. Z (m) * | Ground Level (m) | Bore Dia. DN (mm) | Pipe Material / Wall Thickness | Remarks (valves, bends, air valves, crossings)
0
SUMMARY (calculated automatically — do not edit)
Item | Value | Unit | Description
Nodes entered | 0 | nr | rows with centreline elevation entered
Total pipeline length L |  | m | upstream to downstream, horizontally
Upstream centreline level |  | m | taken from the first node
Downstream centreline level |  | m | taken from the last node entered
Highest centreline level |  | m | critical for downsurge / column separation
Lowest centreline level |  | m | critical for static pressure
Maximum static difference |  | m | highest minus lowest along the route

## 05 Notes
NOTES AND DATA CHECKLIST
Please return this sheet completed; the items below are what delays a surge study most often.
* = MANDATORY — must be filled in (darker blue shading). All other fields are optional.
Purpose | This workbook collects the data required to build a surge (water hammer) model of a pumping main and to size its protection scheme. Sheets: 01 General → 02 Pump Data → 03 Reservoir Levels → 04 Pipeline Profile → these notes.
Datum & units | Every level must be on the same datum (e.g. national datum, local assumed datum). Please state the datum used. SI units are used throughout; if your drawings are in imperial units, either convert or send them as they are and mark clearly which is which.
Pump data | Qn, Hn, n and η come from the pump manufacturer’s duty point or certified curves. The rotating inertia J (pump rotor + motor rotor + coupling) must be requested from the manufacturer — it drives the run-down behaviour and therefore the whole downsurge. If it cannot be supplied, say so and it will be estimated from comparable units.
Still to attach | (1) pump Q-H and Q-η curves, and the four-quadrant curves if available; (2) pump installation level and NPSH; (3) valve type, size and closing law; (4) pipe material, wall thickness and Young’s modulus, for wave speed; (5) air valves, surge vessels, tank sizes and locations already foreseen.
Profile practice | Include every change in diameter, every change in gradient, and every summit and depression: summits govern downsurge and column separation, depressions govern envelope pressure rating. Note all air valves, washouts, crossings and major branches in the remarks column.
Scenarios | As a minimum the following are studied: steady state at design flow; simultaneous trip of the running pumps; closure of the delivery main valve; and the worst single-pump or partial-load case. Minimum practical: 4 runs per pipeline.
Acceptance | Commonly applied criteria: minimum transient head should stay above about −7 m to −10 m gauge (to avoid column separation and pipe instability); maximum transient head should stay within the pressure class of the pipe and equipment. Protection may combine air valves, surge anticipation valves, bladder/hydropneumatic vessels, standpipes or feed tanks.
Mandatory inputs (*) | Fields marked with an asterisk * are MANDATORY — the surge model cannot be built without them: • 02 Pump Data — Duty / Standby, Rated Flow Qn, Rated Head Hn, Rated Speed n, Rated Efficiency η; • 03 Reservoir Levels — Design W.L. of the upstream suction well and of the downstream delivery tank; • 04 Pipeline Profile — Chainage (station) and pipe Centreline Elevation Z at every node. All other fields are optional and may be left blank if not available. The mandatory cells are shaded in the darker blue. Grey columns (SN, shaft power, GD², step, summary) are calculated automatically — please do not type in them.
Version | V1.0 — add or delete rows to suit the project.